## Summary
HACCP daily report – Cold Room 02 – 31 Aug 2026
JuKo Tech GmbH · Sample report – JuKo platform demo data
Master data
Customer | Riverside DC GmbH
Site | Central warehouse North, Frankfurt am Main
Equipment | Cold Room 02 · Positive cold room · meat and dairy
Measuring point | Room-air probe, measuring point KR02-T1
Period | Monday, 31 Aug 2026 · 00:00–23:59
Measuring interval | 1 min · resolution 0.1 °C
Limits | lower limit −2.5 °C · upper limit 4.0 °C
Setpoint | −1.8 °C
Created | 1 Sep 2026, 00:05 (automatic)
Key figures
Figure | Value | Unit | Time / note
Current value | -1.7 | °C | 23:59
Minimum | -2.3 | °C | 08:19
Maximum | 4.3 | °C | 05:59
Average | -1.41 | °C
Time in range | 99.58%
Minutes in range | 1434 | min | / 1440
Deviations | 1 | count
Deviation time | 6 | min | 05:57–06:03
Door openings total | 32 | count
Door-open time total | 55.8 | min
of which delivery | 5 | count | 05:31–06:12 · 31.0 min
Door alarms (> 5 min) | 2 | count | 05:36, 05:50 · acknowledged
of which daytime | 27 | count | 08:00–20:00 · 24.8 min
Defrosts (planned) | 4 | count | 03:00, 09:00, 15:00, 21:00
Defrost time total | 55 | min
Compressor run time | 641 | min | 10 h 41 min
Compressor starts | 36 | count
Longest run | 85 | min | 05:27–06:52
Stop time | 799 | min | 13 h 19 min
Duty cycle | 44.5%
Readings | 1440 | count | 100%
Limit deviation
Start | 05:57
Peak | 4.3
Peak at | 05:59
Last value above limit | 06:02
Back in range | 06:03
Duration (min) | 6
Cause | Goods receipt/delivery, door opened repeatedly (5 openings 05:31–06:12, 31 min in total, longest 14 min)
Corrective action | Door closed, goods put away promptly; core-temperature spot check of the delivered goods: 0.9 °C – goods not affected, released.
Acknowledged | 06:05 – M. Weber, shift supervisor
Defrosts
No. · start–end | Duration (min) | Peak (°C) | Peak at · back ≤ −1.3 °C · type
1 · 03:00–03:12 | 12 | 2 | 03:11 · 03:31 · planned
2 · 09:00–09:16 | 16 | 2.2 | 09:14 · 09:36 · planned
3 · 15:00–15:13 | 13 | 1.6 | 15:12 · 15:28 · planned
4 · 21:00–21:14 | 14 | 2.5 | 21:13 · 21:37 · planned
Data integrity
SHA-256 of the measurement data (CSV UTF-8, columns timestamp;temperature_c;door_open;defrost;compressor;status)
f6931efcba006db5da921035fde8d5730bcef057f448aef2f2c38f571d15a9aa

## Readings
Timestamp | Temperature (°C) | Door open | Defrost active | Compressor on | Status | Lower limit (°C) | Upper limit (°C)
2026-08-31 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:01 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:02 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 00:03 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 00:04 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 00:05 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 00:06 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:07 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:08 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 00:09 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 00:10 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 00:11 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 00:12 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 00:13 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 00:14 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 00:15 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 00:16 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 00:17 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 00:18 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 00:19 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 00:20 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 00:21 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 00:22 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 00:23 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 00:24 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 00:25 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 00:26 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 00:27 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 00:28 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 00:29 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 00:30 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 00:31 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 00:32 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 00:33 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 00:34 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 00:35 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 00:36 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 00:37 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 00:38 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:39 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:40 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:41 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 00:42 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 00:43 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:44 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:45 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:46 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 00:47 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 00:48 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 00:49 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 00:50 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 00:51 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 00:52 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 00:53 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 00:54 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 00:55 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 00:56 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 00:57 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 00:58 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 00:59 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 01:00 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 01:01 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 01:02 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 01:03 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 01:04 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 01:05 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 01:06 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 01:07 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 01:08 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 01:09 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 01:10 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 01:11 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 01:12 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 01:13 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 01:14 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 01:15 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 01:16 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 01:17 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 01:18 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 01:19 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 01:20 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 01:21 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 01:22 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 01:23 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 01:24 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 01:25 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 01:26 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 01:27 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 01:28 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 01:29 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 01:30 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 01:31 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 01:32 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 01:33 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 01:34 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 01:35 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 01:36 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 01:37 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 01:38 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 01:39 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 01:40 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 01:41 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 01:42 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 01:43 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 01:44 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 01:45 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 01:46 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 01:47 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 01:48 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 01:49 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 01:50 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 01:51 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 01:52 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 01:53 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 01:54 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 01:55 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 01:56 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 01:57 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 01:58 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 01:59 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 02:00 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 02:01 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 02:02 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 02:03 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 02:04 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 02:05 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 02:06 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 02:07 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 02:08 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 02:09 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 02:10 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 02:11 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 02:12 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 02:13 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 02:14 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 02:15 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 02:16 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 02:17 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 02:18 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 02:19 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 02:20 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 02:21 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 02:22 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 02:23 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 02:24 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 02:25 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 02:26 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 02:27 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 02:28 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 02:29 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 02:30 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 02:31 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 02:32 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 02:33 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 02:34 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 02:35 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 02:36 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 02:37 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 02:38 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 02:39 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 02:40 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 02:41 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 02:42 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 02:43 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 02:44 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 02:45 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 02:46 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 02:47 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 02:48 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 02:49 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 02:50 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 02:51 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 02:52 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 02:53 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 02:54 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 02:55 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 02:56 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 02:57 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 02:58 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 02:59 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 03:00 | -1.4 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:01 | -1.2 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:02 | -0.8 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:03 | -0.4 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:04 | 0 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:05 | 0.3 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:06 | 0.8 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:07 | 1.1 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:08 | 1.4 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:09 | 1.7 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:10 | 1.9 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:11 | 2 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 03:12 | 1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 03:13 | 1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 03:14 | 1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 03:15 | 1 | no | no | on | OK | -2.5 | 4
2026-08-31 03:16 | 0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 03:17 | 0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 03:18 | 0.3 | no | no | on | OK | -2.5 | 4
2026-08-31 03:19 | 0 | no | no | on | OK | -2.5 | 4
2026-08-31 03:20 | -0.1 | no | no | on | OK | -2.5 | 4
2026-08-31 03:21 | -0.2 | no | no | on | OK | -2.5 | 4
2026-08-31 03:22 | -0.4 | no | no | on | OK | -2.5 | 4
2026-08-31 03:23 | -0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 03:24 | -0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 03:25 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 03:26 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 03:27 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 03:28 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 03:29 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 03:30 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 03:31 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 03:32 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 03:33 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 03:34 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 03:35 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 03:36 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 03:37 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 03:38 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 03:39 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 03:40 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 03:41 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 03:42 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 03:43 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 03:44 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 03:45 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 03:46 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 03:47 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 03:48 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 03:49 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 03:50 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 03:51 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 03:52 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 03:53 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 03:54 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 03:55 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 03:56 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 03:57 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 03:58 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 03:59 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 04:00 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 04:01 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 04:02 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 04:03 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 04:04 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 04:05 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 04:06 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 04:07 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 04:08 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 04:09 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 04:10 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 04:11 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 04:12 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 04:13 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 04:14 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 04:15 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 04:16 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 04:17 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 04:18 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 04:19 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 04:20 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 04:21 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 04:22 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 04:23 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 04:24 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 04:25 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 04:26 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 04:27 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 04:28 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 04:29 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 04:30 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 04:31 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 04:32 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 04:33 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 04:34 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 04:35 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 04:36 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 04:37 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 04:38 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 04:39 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 04:40 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 04:41 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 04:42 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 04:43 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 04:44 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 04:45 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 04:46 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 04:47 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 04:48 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 04:49 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 04:50 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 04:51 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 04:52 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 04:53 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 04:54 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 04:55 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 04:56 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 04:57 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 04:58 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 04:59 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 05:00 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 05:01 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 05:02 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 05:03 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 05:04 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 05:05 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 05:06 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 05:07 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 05:08 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 05:09 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 05:10 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 05:11 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 05:12 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 05:13 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 05:14 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 05:15 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 05:16 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 05:17 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 05:18 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 05:19 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 05:20 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 05:21 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 05:22 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 05:23 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 05:24 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 05:25 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 05:26 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 05:27 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 05:28 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 05:29 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 05:30 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 05:31 | -1.5 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:32 | -1.2 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:33 | -0.4 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:34 | 0.3 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:35 | 1 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:36 | 1.5 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:37 | 1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 05:38 | 1.6 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:39 | 1.2 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:40 | 1.2 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:41 | 1.6 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:42 | 2 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:43 | 2.2 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:44 | 2.5 | no | no | on | OK | -2.5 | 4
2026-08-31 05:45 | 2.3 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:46 | 2.1 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:47 | 2.2 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:48 | 2.5 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:49 | 2.8 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:50 | 3 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:51 | 3.2 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:52 | 3.4 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:53 | 3.6 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:54 | 3.7 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:55 | 3.9 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:56 | 3.9 | yes | no | on | OK | -2.5 | 4
2026-08-31 05:57 | 4.1 | yes | no | on | Deviation | -2.5 | 4
2026-08-31 05:58 | 4.1 | yes | no | on | Deviation | -2.5 | 4
2026-08-31 05:59 | 4.3 | yes | no | on | Deviation | -2.5 | 4
2026-08-31 06:00 | 4.1 | yes | no | on | Deviation | -2.5 | 4
2026-08-31 06:01 | 4.1 | yes | no | on | Deviation | -2.5 | 4
2026-08-31 06:02 | 4.1 | yes | no | on | Deviation | -2.5 | 4
2026-08-31 06:03 | 4 | no | no | on | OK | -2.5 | 4
2026-08-31 06:04 | 3.6 | no | no | on | OK | -2.5 | 4
2026-08-31 06:05 | 3 | no | no | on | OK | -2.5 | 4
2026-08-31 06:06 | 2.5 | no | no | on | OK | -2.5 | 4
2026-08-31 06:07 | 2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 06:08 | 1.8 | yes | no | on | OK | -2.5 | 4
2026-08-31 06:09 | 1.7 | yes | no | on | OK | -2.5 | 4
2026-08-31 06:10 | 2 | yes | no | on | OK | -2.5 | 4
2026-08-31 06:11 | 2.5 | yes | no | on | OK | -2.5 | 4
2026-08-31 06:12 | 3 | yes | no | on | OK | -2.5 | 4
2026-08-31 06:13 | 3.5 | no | no | on | OK | -2.5 | 4
2026-08-31 06:14 | 3.3 | no | no | on | OK | -2.5 | 4
2026-08-31 06:15 | 2.9 | no | no | on | OK | -2.5 | 4
2026-08-31 06:16 | 2.5 | no | no | on | OK | -2.5 | 4
2026-08-31 06:17 | 2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 06:18 | 1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 06:19 | 1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 06:20 | 1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 06:21 | 0.9 | no | no | on | OK | -2.5 | 4
2026-08-31 06:22 | 0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 06:23 | 0.6 | no | no | on | OK | -2.5 | 4
2026-08-31 06:24 | 0.4 | no | no | on | OK | -2.5 | 4
2026-08-31 06:25 | 0.3 | no | no | on | OK | -2.5 | 4
2026-08-31 06:26 | 0.2 | no | no | on | OK | -2.5 | 4
2026-08-31 06:27 | 0 | no | no | on | OK | -2.5 | 4
2026-08-31 06:28 | -0.1 | no | no | on | OK | -2.5 | 4
2026-08-31 06:29 | -0.1 | no | no | on | OK | -2.5 | 4
2026-08-31 06:30 | -0.2 | no | no | on | OK | -2.5 | 4
2026-08-31 06:31 | -0.3 | no | no | on | OK | -2.5 | 4
2026-08-31 06:32 | -0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 06:33 | -0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 06:34 | -0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 06:35 | -0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 06:36 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 06:37 | -0.9 | no | no | on | OK | -2.5 | 4
2026-08-31 06:38 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 06:39 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 06:40 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 06:41 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 06:42 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 06:43 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 06:44 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 06:45 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 06:46 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 06:47 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 06:48 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 06:49 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 06:50 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 06:51 | -2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 06:52 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 06:53 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 06:54 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 06:55 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 06:56 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 06:57 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 06:58 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 06:59 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 07:00 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 07:01 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 07:02 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:03 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:04 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 07:05 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 07:06 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 07:07 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 07:08 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 07:09 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 07:10 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 07:11 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 07:12 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 07:13 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 07:14 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 07:15 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 07:16 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 07:17 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 07:18 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 07:19 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 07:20 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 07:21 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 07:22 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 07:23 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 07:24 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 07:25 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 07:26 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 07:27 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 07:28 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 07:29 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 07:30 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 07:31 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 07:32 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 07:33 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 07:34 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:35 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:36 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:37 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:38 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:39 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 07:40 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 07:41 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:42 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 07:43 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:44 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 07:45 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 07:46 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 07:47 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 07:48 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 07:49 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 07:50 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 07:51 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 07:52 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 07:53 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 07:54 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 07:55 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 07:56 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 07:57 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 07:58 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 07:59 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 08:00 | -1.4 | yes | no | on | OK | -2.5 | 4
2026-08-31 08:01 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 08:02 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 08:03 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 08:04 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 08:05 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 08:06 | -1.6 | yes | no | on | OK | -2.5 | 4
2026-08-31 08:07 | -1.7 | yes | no | on | OK | -2.5 | 4
2026-08-31 08:08 | -1.4 | yes | no | on | OK | -2.5 | 4
2026-08-31 08:09 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 08:10 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 08:11 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 08:12 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 08:13 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 08:14 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 08:15 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 08:16 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 08:17 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 08:18 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 08:19 | -2.3 | no | no | off | OK | -2.5 | 4
2026-08-31 08:20 | -2.3 | no | no | off | OK | -2.5 | 4
2026-08-31 08:21 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 08:22 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 08:23 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 08:24 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 08:25 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 08:26 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 08:27 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 08:28 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 08:29 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 08:30 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 08:31 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 08:32 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 08:33 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 08:34 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 08:35 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 08:36 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 08:37 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 08:38 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 08:39 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 08:40 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 08:41 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 08:42 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 08:43 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 08:44 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 08:45 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 08:46 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 08:47 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 08:48 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 08:49 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 08:50 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 08:51 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 08:52 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 08:53 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 08:54 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 08:55 | -2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 08:56 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 08:57 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 08:58 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 08:59 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 09:00 | -2.1 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:01 | -1.9 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:02 | -1.6 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:03 | -1.2 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:04 | -0.8 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:05 | -0.4 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:06 | 0 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:07 | 0.3 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:08 | 0.7 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:09 | 1 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:10 | 1.3 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:11 | 1.5 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:12 | 1.8 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:13 | 2 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:14 | 2.2 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:15 | 2.2 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 09:16 | 2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 09:17 | 1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 09:18 | 1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 09:19 | 1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 09:20 | 0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 09:21 | 0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 09:22 | 0.3 | no | no | on | OK | -2.5 | 4
2026-08-31 09:23 | 0 | no | no | on | OK | -2.5 | 4
2026-08-31 09:24 | -0.1 | no | no | on | OK | -2.5 | 4
2026-08-31 09:25 | -0.2 | no | no | on | OK | -2.5 | 4
2026-08-31 09:26 | -0.4 | no | no | on | OK | -2.5 | 4
2026-08-31 09:27 | -0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 09:28 | -0.6 | no | no | on | OK | -2.5 | 4
2026-08-31 09:29 | -0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 09:30 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 09:31 | -0.9 | no | no | on | OK | -2.5 | 4
2026-08-31 09:32 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 09:33 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 09:34 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 09:35 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 09:36 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 09:37 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 09:38 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 09:39 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 09:40 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 09:41 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 09:42 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 09:43 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 09:44 | -1.8 | yes | no | on | OK | -2.5 | 4
2026-08-31 09:45 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 09:46 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 09:47 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 09:48 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 09:49 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 09:50 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 09:51 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 09:52 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 09:53 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 09:54 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 09:55 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 09:56 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 09:57 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 09:58 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 09:59 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 10:00 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 10:01 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 10:02 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 10:03 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 10:04 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 10:05 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 10:06 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 10:07 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 10:08 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 10:09 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 10:10 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 10:11 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 10:12 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 10:13 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 10:14 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 10:15 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 10:16 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 10:17 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 10:18 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 10:19 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 10:20 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 10:21 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 10:22 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 10:23 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 10:24 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 10:25 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 10:26 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 10:27 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 10:28 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 10:29 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 10:30 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 10:31 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 10:32 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 10:33 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 10:34 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 10:35 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 10:36 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 10:37 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 10:38 | -2 | yes | no | off | OK | -2.5 | 4
2026-08-31 10:39 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 10:40 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 10:41 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 10:42 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 10:43 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 10:44 | -1.5 | yes | no | off | OK | -2.5 | 4
2026-08-31 10:45 | -1.5 | yes | no | off | OK | -2.5 | 4
2026-08-31 10:46 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 10:47 | -0.9 | no | no | on | OK | -2.5 | 4
2026-08-31 10:48 | -0.9 | no | no | on | OK | -2.5 | 4
2026-08-31 10:49 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 10:50 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 10:51 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 10:52 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 10:53 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 10:54 | -1.7 | yes | no | on | OK | -2.5 | 4
2026-08-31 10:55 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 10:56 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 10:57 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 10:58 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 10:59 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 11:00 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 11:01 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:02 | -2.1 | yes | no | off | OK | -2.5 | 4
2026-08-31 11:03 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 11:04 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:05 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:06 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:07 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:08 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:09 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:10 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:11 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 11:12 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 11:13 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 11:14 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 11:15 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 11:16 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 11:17 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 11:18 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 11:19 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 11:20 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 11:21 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 11:22 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 11:23 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 11:24 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 11:25 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 11:26 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 11:27 | -1.3 | yes | no | on | OK | -2.5 | 4
2026-08-31 11:28 | -1.3 | yes | no | on | OK | -2.5 | 4
2026-08-31 11:29 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 11:30 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 11:31 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 11:32 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 11:33 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 11:34 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 11:35 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 11:36 | -1.6 | yes | no | on | OK | -2.5 | 4
2026-08-31 11:37 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 11:38 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 11:39 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 11:40 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 11:41 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 11:42 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 11:43 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 11:44 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 11:45 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:46 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:47 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:48 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 11:49 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 11:50 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 11:51 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 11:52 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 11:53 | -2 | yes | no | off | OK | -2.5 | 4
2026-08-31 11:54 | -1.9 | yes | no | off | OK | -2.5 | 4
2026-08-31 11:55 | -1.4 | yes | no | off | OK | -2.5 | 4
2026-08-31 11:56 | -0.8 | yes | no | on | OK | -2.5 | 4
2026-08-31 11:57 | -0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 11:58 | -0.6 | yes | no | on | OK | -2.5 | 4
2026-08-31 11:59 | -0.6 | no | no | on | OK | -2.5 | 4
2026-08-31 12:00 | -0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 12:01 | -0.9 | no | no | on | OK | -2.5 | 4
2026-08-31 12:02 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 12:03 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 12:04 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 12:05 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 12:06 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 12:07 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 12:08 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 12:09 | -2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 12:10 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 12:11 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:12 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:13 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:14 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:15 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:16 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:17 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:18 | -2.2 | yes | no | off | OK | -2.5 | 4
2026-08-31 12:19 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:20 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 12:21 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 12:22 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 12:23 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 12:24 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 12:25 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 12:26 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 12:27 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 12:28 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 12:29 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 12:30 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 12:31 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 12:32 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 12:33 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 12:34 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 12:35 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 12:36 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 12:37 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 12:38 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 12:39 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 12:40 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 12:41 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 12:42 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 12:43 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 12:44 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 12:45 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 12:46 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 12:47 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 12:48 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 12:49 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:50 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:51 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 12:52 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 12:53 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:54 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 12:55 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 12:56 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:57 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 12:58 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 12:59 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 13:00 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 13:01 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 13:02 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 13:03 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 13:04 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 13:05 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 13:06 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 13:07 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 13:08 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 13:09 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 13:10 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 13:11 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 13:12 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 13:13 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 13:14 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 13:15 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 13:16 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 13:17 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 13:18 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 13:19 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 13:20 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 13:21 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 13:22 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 13:23 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 13:24 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 13:25 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 13:26 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 13:27 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:28 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:29 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 13:30 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:31 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:32 | -2.1 | yes | no | off | OK | -2.5 | 4
2026-08-31 13:33 | -1.8 | yes | no | off | OK | -2.5 | 4
2026-08-31 13:34 | -1.3 | yes | no | on | OK | -2.5 | 4
2026-08-31 13:35 | -0.7 | yes | no | on | OK | -2.5 | 4
2026-08-31 13:36 | -0.4 | no | no | on | OK | -2.5 | 4
2026-08-31 13:37 | -0.4 | no | no | on | OK | -2.5 | 4
2026-08-31 13:38 | -0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 13:39 | -0.9 | no | no | on | OK | -2.5 | 4
2026-08-31 13:40 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 13:41 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 13:42 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 13:43 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 13:44 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 13:45 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 13:46 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:47 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:48 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 13:49 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 13:50 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 13:51 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 13:52 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:53 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:54 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:55 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 13:56 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 13:57 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 13:58 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 13:59 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 14:00 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 14:01 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 14:02 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 14:03 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 14:04 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 14:05 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 14:06 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 14:07 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 14:08 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 14:09 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 14:10 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:11 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 14:12 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:13 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:14 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:15 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:16 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 14:17 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 14:18 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 14:19 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 14:20 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 14:21 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 14:22 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 14:23 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 14:24 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 14:25 | -2.1 | yes | no | off | OK | -2.5 | 4
2026-08-31 14:26 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 14:27 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 14:28 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 14:29 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 14:30 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 14:31 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 14:32 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 14:33 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 14:34 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 14:35 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 14:36 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 14:37 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 14:38 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 14:39 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 14:40 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 14:41 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 14:42 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 14:43 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 14:44 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:45 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:46 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 14:47 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:48 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:49 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 14:50 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 14:51 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 14:52 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 14:53 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 14:54 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 14:55 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 14:56 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 14:57 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 14:58 | -2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 14:59 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 15:00 | -2.1 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:01 | -2 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:02 | -1.7 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:03 | -1.2 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:04 | -0.8 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:05 | -0.4 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:06 | -0.1 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:07 | 0.3 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:08 | 0.7 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:09 | 0.9 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:10 | 1.2 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:11 | 1.5 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:12 | 1.6 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 15:13 | 1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 15:14 | 1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 15:15 | 0.9 | no | no | on | OK | -2.5 | 4
2026-08-31 15:16 | 0.6 | no | no | on | OK | -2.5 | 4
2026-08-31 15:17 | 0.3 | no | no | on | OK | -2.5 | 4
2026-08-31 15:18 | 0 | no | no | on | OK | -2.5 | 4
2026-08-31 15:19 | -0.2 | no | no | on | OK | -2.5 | 4
2026-08-31 15:20 | -0.4 | no | no | on | OK | -2.5 | 4
2026-08-31 15:21 | -0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 15:22 | -0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 15:23 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 15:24 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 15:25 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 15:26 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 15:27 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 15:28 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 15:29 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 15:30 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 15:31 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 15:32 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 15:33 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 15:34 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 15:35 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 15:36 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 15:37 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 15:38 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 15:39 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 15:40 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 15:41 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 15:42 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 15:43 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 15:44 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 15:45 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 15:46 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 15:47 | -2 | yes | no | off | OK | -2.5 | 4
2026-08-31 15:48 | -1.8 | yes | no | off | OK | -2.5 | 4
2026-08-31 15:49 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 15:50 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 15:51 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 15:52 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 15:53 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 15:54 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 15:55 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 15:56 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 15:57 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 15:58 | -2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 15:59 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 16:00 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 16:01 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 16:02 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 16:03 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 16:04 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 16:05 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 16:06 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 16:07 | -2 | yes | no | off | OK | -2.5 | 4
2026-08-31 16:08 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 16:09 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 16:10 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 16:11 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 16:12 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 16:13 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 16:14 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 16:15 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 16:16 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 16:17 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 16:18 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 16:19 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 16:20 | -1.3 | yes | no | on | OK | -2.5 | 4
2026-08-31 16:21 | -1.2 | yes | no | on | OK | -2.5 | 4
2026-08-31 16:22 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 16:23 | -0.6 | no | no | on | OK | -2.5 | 4
2026-08-31 16:24 | -0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 16:25 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 16:26 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 16:27 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 16:28 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 16:29 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 16:30 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 16:31 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 16:32 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 16:33 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 16:34 | -1.8 | yes | no | on | OK | -2.5 | 4
2026-08-31 16:35 | -1.9 | yes | no | on | OK | -2.5 | 4
2026-08-31 16:36 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 16:37 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 16:38 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 16:39 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 16:40 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 16:41 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 16:42 | -2.3 | no | no | off | OK | -2.5 | 4
2026-08-31 16:43 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 16:44 | -2.3 | no | no | off | OK | -2.5 | 4
2026-08-31 16:45 | -2.3 | no | no | off | OK | -2.5 | 4
2026-08-31 16:46 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 16:47 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 16:48 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 16:49 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 16:50 | -2 | yes | no | off | OK | -2.5 | 4
2026-08-31 16:51 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 16:52 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 16:53 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 16:54 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 16:55 | -1.6 | yes | no | off | OK | -2.5 | 4
2026-08-31 16:56 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 16:57 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 16:58 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 16:59 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 17:00 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 17:01 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 17:02 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 17:03 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 17:04 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 17:05 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 17:06 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 17:07 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 17:08 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 17:09 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:10 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:11 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 17:12 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:13 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 17:14 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:15 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:16 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 17:17 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 17:18 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 17:19 | -1.9 | yes | no | off | OK | -2.5 | 4
2026-08-31 17:20 | -1.9 | yes | no | off | OK | -2.5 | 4
2026-08-31 17:21 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 17:22 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 17:23 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 17:24 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 17:25 | -1.4 | yes | no | on | OK | -2.5 | 4
2026-08-31 17:26 | -1.5 | yes | no | on | OK | -2.5 | 4
2026-08-31 17:27 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 17:28 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 17:29 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 17:30 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 17:31 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 17:32 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 17:33 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 17:34 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:35 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:36 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 17:37 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:38 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 17:39 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:40 | -2.1 | yes | no | off | OK | -2.5 | 4
2026-08-31 17:41 | -2 | yes | no | off | OK | -2.5 | 4
2026-08-31 17:42 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 17:43 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 17:44 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 17:45 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 17:46 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 17:47 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 17:48 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 17:49 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 17:50 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 17:51 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 17:52 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:53 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:54 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 17:55 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 17:56 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:57 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:58 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 17:59 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:00 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:01 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:02 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 18:03 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 18:04 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 18:05 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 18:06 | -1.7 | yes | no | off | OK | -2.5 | 4
2026-08-31 18:07 | -1.6 | yes | no | off | OK | -2.5 | 4
2026-08-31 18:08 | -1.1 | yes | no | on | OK | -2.5 | 4
2026-08-31 18:09 | -0.5 | yes | no | on | OK | -2.5 | 4
2026-08-31 18:10 | -0.1 | no | no | on | OK | -2.5 | 4
2026-08-31 18:11 | 0 | no | no | on | OK | -2.5 | 4
2026-08-31 18:12 | -0.3 | no | no | on | OK | -2.5 | 4
2026-08-31 18:13 | -0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 18:14 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 18:15 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 18:16 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 18:17 | -1.3 | yes | no | on | OK | -2.5 | 4
2026-08-31 18:18 | -1.4 | yes | no | on | OK | -2.5 | 4
2026-08-31 18:19 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 18:20 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 18:21 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 18:22 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 18:23 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 18:24 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 18:25 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 18:26 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 18:27 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 18:28 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:29 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 18:30 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:31 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:32 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:33 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 18:34 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 18:35 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:36 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:37 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:38 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 18:39 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 18:40 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 18:41 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 18:42 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 18:43 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 18:44 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 18:45 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 18:46 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 18:47 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 18:48 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 18:49 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 18:50 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 18:51 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 18:52 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 18:53 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 18:54 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 18:55 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 18:56 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 18:57 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 18:58 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 18:59 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 19:00 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 19:01 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 19:02 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 19:03 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 19:04 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 19:05 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 19:06 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 19:07 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:08 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:09 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 19:10 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:11 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:12 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 19:13 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:14 | -2 | yes | no | off | OK | -2.5 | 4
2026-08-31 19:15 | -1.7 | yes | no | off | OK | -2.5 | 4
2026-08-31 19:16 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 19:17 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 19:18 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 19:19 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 19:20 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 19:21 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 19:22 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 19:23 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 19:24 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 19:25 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 19:26 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:27 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:28 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:29 | -2.3 | no | no | off | OK | -2.5 | 4
2026-08-31 19:30 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:31 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:32 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 19:33 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 19:34 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 19:35 | -2.1 | yes | no | off | OK | -2.5 | 4
2026-08-31 19:36 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 19:37 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 19:38 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 19:39 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 19:40 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 19:41 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 19:42 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 19:43 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 19:44 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 19:45 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 19:46 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 19:47 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 19:48 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 19:49 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 19:50 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 19:51 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 19:52 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 19:53 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 19:54 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 19:55 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 19:56 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 19:57 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 19:58 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 19:59 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 20:00 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 20:01 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 20:02 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 20:03 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 20:04 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:05 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:06 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 20:07 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 20:08 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 20:09 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 20:10 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:11 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:12 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 20:13 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 20:14 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 20:15 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 20:16 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 20:17 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 20:18 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 20:19 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 20:20 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 20:21 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 20:22 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 20:23 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 20:24 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 20:25 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 20:26 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 20:27 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 20:28 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 20:29 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 20:30 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 20:31 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 20:32 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 20:33 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 20:34 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 20:35 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 20:36 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 20:37 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 20:38 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 20:39 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 20:40 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 20:41 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:42 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:43 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 20:44 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:45 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:46 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:47 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:48 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 20:49 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 20:50 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 20:51 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 20:52 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 20:53 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 20:54 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 20:55 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 20:56 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 20:57 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 20:58 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 20:59 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 21:00 | -1.5 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:01 | -1.3 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:02 | -0.9 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:03 | -0.5 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:04 | -0.1 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:05 | 0.3 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:06 | 0.7 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:07 | 1 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:08 | 1.4 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:09 | 1.6 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:10 | 1.9 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:11 | 2.1 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:12 | 2.4 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:13 | 2.5 | no | yes | off | Defrost | -2.5 | 4
2026-08-31 21:14 | 2.3 | no | no | on | OK | -2.5 | 4
2026-08-31 21:15 | 2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 21:16 | 1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 21:17 | 1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 21:18 | 1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 21:19 | 0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 21:20 | 0.6 | no | no | on | OK | -2.5 | 4
2026-08-31 21:21 | 0.3 | no | no | on | OK | -2.5 | 4
2026-08-31 21:22 | 0.2 | no | no | on | OK | -2.5 | 4
2026-08-31 21:23 | 0 | no | no | on | OK | -2.5 | 4
2026-08-31 21:24 | -0.1 | no | no | on | OK | -2.5 | 4
2026-08-31 21:25 | -0.2 | no | no | on | OK | -2.5 | 4
2026-08-31 21:26 | -0.3 | no | no | on | OK | -2.5 | 4
2026-08-31 21:27 | -0.4 | no | no | on | OK | -2.5 | 4
2026-08-31 21:28 | -0.5 | no | no | on | OK | -2.5 | 4
2026-08-31 21:29 | -0.6 | no | no | on | OK | -2.5 | 4
2026-08-31 21:30 | -0.7 | no | no | on | OK | -2.5 | 4
2026-08-31 21:31 | -0.8 | no | no | on | OK | -2.5 | 4
2026-08-31 21:32 | -0.9 | no | no | on | OK | -2.5 | 4
2026-08-31 21:33 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 21:34 | -1 | no | no | on | OK | -2.5 | 4
2026-08-31 21:35 | -1.1 | no | no | on | OK | -2.5 | 4
2026-08-31 21:36 | -1.2 | no | no | on | OK | -2.5 | 4
2026-08-31 21:37 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 21:38 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 21:39 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 21:40 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 21:41 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 21:42 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 21:43 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 21:44 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 21:45 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 21:46 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 21:47 | -2.1 | no | no | on | OK | -2.5 | 4
2026-08-31 21:48 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 21:49 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 21:50 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 21:51 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 21:52 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 21:53 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 21:54 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 21:55 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 21:56 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 21:57 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 21:58 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 21:59 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 22:00 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 22:01 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 22:02 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 22:03 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 22:04 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 22:05 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 22:06 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 22:07 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 22:08 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 22:09 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 22:10 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 22:11 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 22:12 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:13 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:14 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:15 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:16 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:17 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 22:18 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 22:19 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 22:20 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 22:21 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 22:22 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 22:23 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 22:24 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 22:25 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 22:26 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 22:27 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 22:28 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 22:29 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 22:30 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 22:31 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 22:32 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 22:33 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 22:34 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 22:35 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 22:36 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 22:37 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 22:38 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 22:39 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 22:40 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 22:41 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 22:42 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 22:43 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 22:44 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 22:45 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 22:46 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 22:47 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 22:48 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 22:49 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 22:50 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:51 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:52 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 22:53 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:54 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:55 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 22:56 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 22:57 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 22:58 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 22:59 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 23:00 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 23:01 | -1.8 | no | no | on | OK | -2.5 | 4
2026-08-31 23:02 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 23:03 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 23:04 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 23:05 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 23:06 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 23:07 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:08 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 23:09 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 23:10 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 23:11 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 23:12 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:13 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:14 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 23:15 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 23:16 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 23:17 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 23:18 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 23:19 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 23:20 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 23:21 | -1.7 | no | no | off | OK | -2.5 | 4
2026-08-31 23:22 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 23:23 | -1.6 | no | no | off | OK | -2.5 | 4
2026-08-31 23:24 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 23:25 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 23:26 | -1.5 | no | no | off | OK | -2.5 | 4
2026-08-31 23:27 | -1.4 | no | no | off | OK | -2.5 | 4
2026-08-31 23:28 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 23:29 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 23:30 | -1.3 | no | no | on | OK | -2.5 | 4
2026-08-31 23:31 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 23:32 | -1.4 | no | no | on | OK | -2.5 | 4
2026-08-31 23:33 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 23:34 | -1.5 | no | no | on | OK | -2.5 | 4
2026-08-31 23:35 | -1.6 | no | no | on | OK | -2.5 | 4
2026-08-31 23:36 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 23:37 | -1.7 | no | no | on | OK | -2.5 | 4
2026-08-31 23:38 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 23:39 | -1.9 | no | no | on | OK | -2.5 | 4
2026-08-31 23:40 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 23:41 | -2 | no | no | on | OK | -2.5 | 4
2026-08-31 23:42 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 23:43 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:44 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:45 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:46 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:47 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:48 | -2.2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:49 | -2.1 | no | no | off | OK | -2.5 | 4
2026-08-31 23:50 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:51 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:52 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:53 | -2 | no | no | off | OK | -2.5 | 4
2026-08-31 23:54 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 23:55 | -1.9 | no | no | off | OK | -2.5 | 4
2026-08-31 23:56 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 23:57 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 23:58 | -1.8 | no | no | off | OK | -2.5 | 4
2026-08-31 23:59 | -1.7 | no | no | off | OK | -2.5 | 4

## Events
Time | Type | Status | Event | Value | Duration
03:00 | Defrost | Info | Defrost 1 of 4 (planned) | peak 2.0 °C | 12 min
05:31 | Delivery | Info | Delivery: door opened 5× (05:31–06:12), longest opening 14 min | — | 31 min
05:31:10 | Delivery | Info | Door opening (delivery) 05:31:10–05:36:40 | — | 5 min 30 s
05:36 | Door alarm | Warning | Door open longer than 5 min – alarm (delivery), acknowledged 05:38 (M. Weber) | — | 5 min 30 s
05:38:50 | Delivery | Info | Door opening (delivery) 05:38:50–05:43:50 | — | 5 min
05:45:20 | Delivery | Info | Door opening (delivery) 05:45:20–05:59:20 | — | 14 min
05:50 | Door alarm | Warning | Door open longer than 5 min – alarm (delivery), acknowledged 05:52 (M. Weber) | — | 14 min
05:57 | Deviation | Warning | Upper limit 4.0 °C exceeded – alarm sent to shift supervisor | 4.1 °C | 6 min
05:59 | Deviation | Warning | Peak of the deviation | 4.3 °C | —
06:00:00 | Delivery | Info | Door opening (delivery) 06:00:00–06:02:10 | — | 2 min 10 s
06:03 | Deviation | OK | Back in range (deviation 6 min) | 4.0 °C | —
06:05 | Action | OK | Alarm acknowledged, corrective action documented (M. Weber, shift supervisor) | — | —
06:08:30 | Delivery | Info | Door opening (delivery) 06:08:30–06:12:50 | — | 4 min 20 s
08:00:30 | Door opening | Info | Door opening 08:00:30–08:01:00 | — | 30 s
08:06:50 | Door opening | Info | Door opening 08:06:50–08:08:10 | — | 1 min 20 s
09:00 | Defrost | Info | Defrost 2 of 4 (planned) | peak 2.2 °C | 16 min
09:44:00 | Door opening | Info | Door opening 09:44:00–09:44:20 | — | 20 s
10:38:10 | Door opening | Info | Door opening 10:38:10–10:38:50 | — | 40 s
10:44:50 | Door opening | Info | Door opening 10:44:50–10:46:00 | — | 1 min 10 s
10:54:30 | Door opening | Info | Door opening 10:54:30–10:54:50 | — | 20 s
11:02:20 | Door opening | Info | Door opening 11:02:20–11:02:50 | — | 30 s
11:27:50 | Door opening | Info | Door opening 11:27:50–11:28:30 | — | 40 s
11:36:40 | Door opening | Info | Door opening 11:36:40–11:37:00 | — | 20 s
11:53:40 | Door opening | Info | Door opening 11:53:40–11:56:10 | — | 2 min 30 s
11:58:10 | Door opening | Info | Door opening 11:58:10–11:58:40 | — | 30 s
12:18:30 | Door opening | Info | Door opening 12:18:30–12:18:50 | — | 20 s
13:32:20 | Door opening | Info | Door opening 13:32:20–13:35:20 | — | 3 min
14:25:20 | Door opening | Info | Door opening 14:25:20–14:26:00 | — | 40 s
15:00 | Defrost | Info | Defrost 3 of 4 (planned) | peak 1.6 °C | 13 min
15:47:20 | Door opening | Info | Door opening 15:47:20–15:48:20 | — | 1 min
16:07:10 | Door opening | Info | Door opening 16:07:10–16:07:30 | — | 20 s
16:20:30 | Door opening | Info | Door opening 16:20:30–16:21:50 | — | 1 min 20 s
16:34:50 | Door opening | Info | Door opening 16:34:50–16:35:20 | — | 30 s
16:50:00 | Door opening | Info | Door opening 16:50:00–16:50:30 | — | 30 s
16:55:20 | Door opening | Info | Door opening 16:55:20–16:55:50 | — | 30 s
17:19:40 | Door opening | Info | Door opening 17:19:40–17:20:30 | — | 50 s
17:25:50 | Door opening | Info | Door opening 17:25:50–17:26:10 | — | 20 s
17:40:30 | Door opening | Info | Door opening 17:40:30–17:41:30 | — | 1 min
18:06:40 | Door opening | Info | Door opening 18:06:40–18:09:40 | — | 3 min
18:17:30 | Door opening | Info | Door opening 18:17:30–18:18:40 | — | 1 min 10 s
19:14:10 | Door opening | Info | Door opening 19:14:10–19:15:10 | — | 1 min
19:35:30 | Door opening | Info | Door opening 19:35:30–19:36:00 | — | 30 s
21:00 | Defrost | Info | Defrost 4 of 4 (planned) | peak 2.5 °C | 14 min
1 Sep · 00:05 | Report | Info | Daily report created (PDF/Excel) | — | —